| TO RECEIVE A PRICE QUOTE, PLEASE COPMLETE THIS FORM AND RETURN TO PANINI: |  |  |  |
| --- | --- | --- | --- |
| Panini S.r.l., Attn: Sales Department |  | TEL: | +39 0536.94.07.07 |
| Via Dino Taruffi, 70 |  | FAX. | +39 0536.94.37.05 |
| 41053 Maranello MO Italia |  | E-MAIL: | mailbox@op-panini.it |

| NAME: |  |  | DATE: |  |
| --- | --- | --- | --- | --- |
| COMPANY: |  |  | TEL: |  |
| ADDRESS: |  |  | FAX: |  |
|  |  |  | E-MAIL: |  |

| MODEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| VAPORAPID–V | VAPORAPID–O | SPRINT | SPECIAL | ECOVAP |
| 1,2 MPa | 1,2 MPa | 1,2 MPa | 1,2 o 1,5 MPa | 1,2 o 1,5 MPa |
| 45–1000 Kg/h | 400–3000 Kg/h | 660–4000 Kg/h | 2400–4000 Kg/h | 4000–20.000 Kg/h |

| MODEL: |  |  | STEAM: |  | KG/H | PRESSURE: |  | MPa | N° BOILERS |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| BURNER: |  1-Stage  2-Stage  Modulating |
| --- | --- |

| FUEL: |  Methane Gas | GAS MAINS PRESSURE: |  | MBAR |
| --- | --- | --- | --- | --- |

|  |  Light Oil (diesel)  Medium Oil 3-5 °E at 50°C  Heavy Oil >7°E at 50°C |
| --- | --- |

| ACCESSORIES (only for Sprint, Special and Ecovap models) |  |  |  |
| --- | --- | --- | --- |
| WATER LEVEL KIT: |  Min/Max  Constant | { | Min/Max uses the classic min and max probes to control the water pump. Constant maintains the same water level by regulating pneumatic valves. |
| PUMP KIT: |  Single  Double | { | The double pump allows repairing or substituting one pump while the boiler continues to function. |
| BLOWDOWN KIT: |  Manual  Automatic | { | Simple manually-actuated valve or automatic blowdown kit with pneumatic valve and electronic timer. |
| PRE-HEATER KIT: |  No  External  Integrated | { | Preheats the carburant air using excess exhaust heat, increasing the boiler yield. Note: the integrated pre-heater is available only for the Special and Ecovap models. |
| INJECTOR KIT: |  Yes  No | { | Safety device that continues water feed in case of a pump error. Suggested only where a backup feed mechanism is mandatory by law. |
| SALINITY KIT: |  Yes  No | { | Automatically drains the salty top water layer when high salt concentrations are measured. |
| O2:ALARM KIT: |  Yes  No | { | Raises an alarm in case of a high stack O2 count, indicating sub-optimal burner calibration. |
| O2 CONTROL KIT: |  Yes  No | { | Automatically calibrates the fuel mixture to keep a constant O2 count at the stack. Requires a special burner. |

| RESERVED FOR PANINI SALES DEPARTMENT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| REC'D BY: |  | DATE REC'D: |  | REQUEST #: |  |
| SENT BY: |  | DATE SENT: |  | OFFER #: |  |

| SMOKE STACK |  |  |  |
| --- | --- | --- | --- |
| SMOKE STACK: |  None  Boiler-based stack  Ground-based stack with connector |  |  |
| CONSTRUCTION: |  Mild Steel  Stainless AISI 304  Stainless AISI 316 |  |  |
| CLADDING: |  None  Aluminum  Stainless AISI 304 |  |  |
| STACK HEIGHT: |  | METERS |  |
| CONNECTOR: |  | METERS | (only for ground-based stack) |

| FEED WATER TANK |  |
| --- | --- |
| The feed water tank provides positive head pressure to the pump and preheats the with condensate return. |  |
| TANK TYPE: |  None  Vertical  Horizontal  Select most adapted for boiler |
| CLADDING: |  None  Polyurethane  Aluminum  Stainless AISI 304 |
| DEOXYGENIZER: |  Include optional thermophysical deoxygenizer module (only for horizontal tank) |

| WATER TREATMENT ACCESSORIES |  |
| --- | --- |
|  Water Filter | Removes from the water particulates and large impurities which foul the water-softener resins and the reverse osmosis membranes. |
|  Dosage Kit | Injects into the water chemical products which remove dissolved oxygen and CO2. |
|  Water Softener | Converts calcium and magnesium salts (that cause scaling) into sodium salts (that don't cause scaling), but does not reduce the total salinity. Select between 2 types:  Single Column. Includes 1 resin tank with a timer which regenerates the resin at predetermined intervals (usually at the end of the workday) whether needed or not.  Double Column. Includes 2 resin tanks and advanced volumetric regeneration (the resins are regenerated only when a predetermined amount of water has passed). |
|  Reverse Osmosis | Removes all hardness ions and impurities, and the majority of dissolved salts, eliminating scaling and sludge buildup. Requires a water softener and the dosage kit. |

| FEED WATER CHARACTERISTICS |  |  |  |  |
| --- | --- | --- | --- | --- |
| To select the size of the water treatment system, attach a chemical analysis of the feed water, or indicate the following water data. If no data are indicated, we will assume the values in parenthesis. Note: these default values are quite high and may lead to unnecessarily large water treatment systems in soft-water areas. |  |  |  |  |
| WATER HARDNESS: |  | °F | (45°F) | Note: 1°F = 10ppm = 0,585gpg |
| CONDENSATE RECOVERY: |  | % | (50%) |  |
| STANDARD WORKDAY: |  | HOURS | (8 HOURS) |  |

ALTRE NOTE